## Last name						Name				matricola

# Section 1. TRUE/FALSE QUESTIONS

- The membrane valve got this name just because has a ceramic membrane in contact with the flowing fluid

true o	false o

- Closed liquid column manometers (“U” tube manometers) containing mercury are used for measuring pressure in a vacuum

true o	false o

- The Coriolis Flowmeter is a transducer of volumetric flowrate

true 	false 

- The sonar level sensors always provide the contemporary measurement of the temperature

true o	false o

# Section 2. MULTIPLE CHOICE QUESTIONS

- Which one is a dimensionless sensor property?

- 	accuracy at the full scale

- 	accuracy at the measured value

- 	rangeability

- 	sensitivity

- The working principle of a pressure transducer can be:

NOTE: check only the wrong answer!

- 	piezoelectric

- 	radio

- 	inductive

- 	electric resistance

- When the percentage variation of flow through a valve equals the percentage variation of plug movement, a valve has a

- 	Linear flow characteristic

- 	Equal percentage flow characteristic

- 	Quick opening flow characteristic

- 	Parabolic flow characteristic

- Which of the following types of level sensors is not used for liquids?

- 	conductive sensor

- 	vibrating sensor

- 	radar sensor

- 	probe sensor

# Section 3: SENSORS AND INSTRUMENTATION FOR PROCESS MEASUREMENTS

## 3.1 Application of a thermocouple

A N-type thermocouple is used to measure the temperature Tgc of a process liquid.

The cold junction of the measuring circuit is at a known temperature: Tgf = 293.16 K.

The voltmeter connected to the cold junction provides a measure of the electromotive force that is

V =  -0.366 mV

- calculate the temperature of the liquid Tgc in ° C, with the approximation of  +/- 1 ° C

## 3.2 The capacitive pressure transducer

- Describe in 3 rows its working principle

## 3.3 The Level sensors: hydrostatic vs. float

- Describe in 3 rows differences between the working principles

## 3.4 The general properties of Sensors

- Describe in 3 rows definition and meaning of repeatability

## 3.5.	Contraction-based flow meters

- Derive the flow equation in the ideal case for liquids

- Use the flow equation to calculate the volumetric flow rate of water in the ideal case where P1=150 kPa, P2=100 kPa, d1=90 mm, d2=20 mm

- Extend the flow equation to the case the flow is not ideal anymore

- Extend the flow equation to fluids with a non-constant density

- Discuss applications, advantages e disadvantages

NB:

A well-organized and short paragraph will be assessed more than a long and confused text!

# Section 4: VALVES

## 4.1. The valve technology and the “Fail–Safe” behavior

- Recognize the type of in the symbol

- What it its application purpose?

- Is it a linear or rotary valve?

- Is it equipped with an external actuator?

- Explain with a short text the action that the valve exerts in the event of a command signal failure

NB: It’s possible to put answers directly on or near the following drawings

## 4.2. Sizing Problem

You’re required to size and to choose a valve for the following conditions:

nominal diameter of the line: DN = 150 mm

fluid: sea water, with a density f = 1.025 kg/L

pressure upstream of the valve: P1 = 2.58 bar

pressure downstream of the valve: P2 = 1.57 bar

nominal flow rate: m = 90 kg/s

vapor pressure: Pv = 4000 Pa

liquid critical pressure ratio factor: FF = 0.956

1. Calculate the flow coefficient Cv for the above conditions

You have a SUN WP "2 piece" full-bore ball valve,

with the following manufacturer’s table of Cv (US gal min-1 psi-½) as a function of the opening angle q (as reported in a row for each DN):

| DN (mm) | Cv (gpm psi-1/2) as a function of the opening angle  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° |
| 40 | 3 | 8 | 10 | 15 | 27 | 58 | 96 | 165 |
| 50 | 5 | 9 | 15 | 23 | 41 | 86 | 140 | 245 |
| 65 | 11 | 18 | 27 | 39 | 71 | 150 | 245 | 410 |
| 80 | 18 | 28 | 44 | 65 | 115 | 245 | 400 | 685 |
| 100 | 26 | 55 | 85 | 130 | 230 | 480 | 785 | 1.275e3 |
| 125 | 45 | 72 | 110 | 165 | 300 | 610 | 1.01e3 | 1.715e3 |
| 150 | 70 | 110 | 168 | 250 | 465 | 980 | 1.615e3 | 2.67e3 |
| 200 | 80 | 135 | 210 | 310 | 540 | 1100 | 1.91e3 | 3.185e3 |

2. Choose the best suitable DN for the valve

3. Plot the intrinsic characteristic of the chosen valve in a diagram

4. Which type is the intrinsic characteristic?

Next, you are requested to insert the chosen valve in a circuit, assuming Pn equal to the original value (P1 - P2) and considering the following three cases for the user pressure drop:

- P2 – P3 = Pu = Pn

- Pu = Pn/2

- Pu = 2Pn

5. How much is the authority V in the 3 cases?

Furthermore, under the condition Pu = 2Pn

- How much is the volumetric flowrate V. passing through the valve for  = 40 °?

- How much is the pressure dropPv, through the valve for  = 40 °?

It is requested to take into account the use of the same valve in the case the pressure upstream of the valve P1 increases by 30% compared to the initial value and the nominal flow rate increases by 50% compared to the initial value:

- For such new flow conditions, is the valve selected in step 2 still suitable? Why?

- For such new flow conditions, does any cavitation occur?